## Sheet1
Voltage Drop Calculation
|  |  | Section |  |  |  |  | Current (Amperes) |  | Voltage Drop
|  |  | From | To | Length (ft) | AWG | Resistance (Ohms/Kft) | At Point | Accum | In Section | Accum | % Drop | Power Loss (W/ft) | At Point
ENTER INFORMATION: | [8 empty] | 0 | .. | .. | .. | ..
Project: | [8 empty] | 0 | .. | .. | .. | ..
Site #: | [8 empty] | 0 | .. | .. | .. | ..
Location: | [8 empty] | 0 | .. | .. | .. | ..
Power Service: | [8 empty] | 0 | .. | .. | .. | ..
Circuit: | [8 empty] | 0 | .. | .. | .. | ..
Sheet #: | [8 empty] | 0 | .. | .. | .. | ..
Supply Voltage: |  | Volts | [6 empty] | 0 | .. | .. | .. | ..
Calculations by: | [8 empty] | 0 | .. | .. | .. | ..
[9 empty] | 0 | .. | .. | .. | ..
[9 empty] | 0 | .. | .. | .. | ..
| Wire Size (AWG) | Resistance (Ohms/Kft)
| 12 | 2.05
| 10 | 1.29
| 8 | 0.809
| 6 | 0.51
| 4 | 0.321
| 3 | 0.254
| 2 | 0.201
| 1 | 0.16
| 1/0 | 0.127
| 2/0 | 0.101
| 3/0 | 0.0797
| 4/0 | 0.0626
Voltage Drop Equations:
Voltage drop in circuit section = (V)
- length includes the length of section with 5-10 ft added to each end, then round up to the closest increment of 5 ft.
)
& Drop = (%)
Power Loss =
Wire Data from 2011 Edition of National Electrical Code, Chapter 9 Table 8
Voltage Drop Equations:
Voltage drop in circuit section =(2∗𝐼∗𝑙∗𝑅" " )/1000 (V)
𝐼=𝐴𝑐𝑐𝑢𝑚𝑢𝑙𝑎𝑡𝑒𝑑 𝐶𝑢𝑟𝑟𝑒𝑛𝑡 𝑖𝑛 𝑆𝑒𝑐𝑡𝑖𝑜𝑛 (𝐴)
𝑙=𝐿𝑒𝑛𝑔𝑡ℎ 𝑜𝑓 𝑠𝑒𝑐𝑡𝑖𝑜𝑛 (𝑓𝑡)
- length includes the length of section with 5-10 ft added to each end, then round up to the closest increment of 5 ft.
𝑅=𝑅𝑒𝑠𝑖𝑠𝑡𝑎𝑛𝑐𝑒 𝑜𝑓 𝑤𝑖𝑟𝑒 (𝛺/1000𝑓𝑡)
& Drop = (𝐴𝑐𝑐𝑢𝑚𝑢𝑙𝑎𝑡𝑒𝑑 𝑉𝑜𝑙𝑡𝑎𝑔𝑒 𝐷𝑟𝑜𝑝)/(𝑆𝑢𝑝𝑝𝑙𝑦 𝑉𝑜𝑙𝑡𝑎𝑔𝑒)∗100 (%)
Power Loss = (𝑣𝑜𝑙𝑡𝑎𝑔𝑒 𝑑𝑟𝑜𝑝 𝑖𝑛 𝑠𝑒𝑐𝑡𝑖𝑜𝑛∗𝑐𝑢𝑟𝑟𝑒𝑛𝑡 𝑎𝑡 𝑝𝑜𝑖𝑛𝑡)/(𝑙𝑒𝑛𝑔𝑡ℎ ) (𝑤𝑎𝑡𝑡𝑠/𝑓𝑡)
Wire Data from 2011 Edition of National Electrical Code, Chapter 9 Table 8
Directions:
1. Fill out all cells under Enter Information:
2. Fill out anything that is bolded in the table
3. Select the corresponding cable size (AWG) so the voltage drop is less than 5%