## Inspection Checklist
Form: | CA-Q-0633_20170120 MF
Ohio Department of Transportation, Division of Construction | [7 empty] | Y
Inspection Quality Checklist | [7 empty] | N
633 Signal Controllers
Header Section |  |  |  |  | Number of Non-Conforming Attributes: | 0
Name: |  | Date Inspected: |  | AltID:
PLN: |  | ContID:
Item No: |  | Project No. (Part Code):
Item Desc:
Location:
Checklist Section
Inspected? | Attribute Inspected | Citation | Inspection Location / Station / Offset | Photo? | Comments / Observations / Measurements | Conforms? (Y / N)
General
| As Per Plan, Miscellaneous, and Special items. In addition to the requirements listed below, do the special “As Per Plan” characteristics conform to the contract documents? Provide a comment describing what was inspected. | Plan |  |  | Required |  | 0
| No applicable Attribute for the Pay Item is listed. Provide a comment describing what was inspected. | Plan |  |  | Required |  | 0
Controller | [6 empty] | 0
| Is the controller properly grounded (max 10 ohms)? Document the Ground Rod Readings | 625.16 / 625.19 |  |  | Required |  | 0
| When a conflict or similar fault occurs, does the conflict monitor cause the intersection to go to flash? | 632.28
| Is the control equipment, terminal blocks, or shelves no closer than 6" to the top of the foundation? | 633.08
Cabinet | [6 empty] | 0
| Is the conduit sealed with a removable sealing compound? No foam sealer! | 633.08 |  |  |  |  | 0
| Are there two (2) sets of equipment lists, operation and maintenance manuals, and board-level schematic and wiring diagrams of the UPS, and the battery data sheets? | 633.05 / UPS Note
| Data key present? | 733.02
| Does the cabinet have the proper finish inside and out as per plan? | 733.03
| Is all the equipment as per plan or ODOT approved? | 733.03
| Is the pole-mounted cabinet at the proper height? Less than 36” high cabinet equal 30” +/- 3”. Over 36” high cabinet equals 23” +/- 3”? | 633.08
| Are all wire terminals tight? | 632.28
| Is the cabinet air filter in place and clean? | 733.03 |  |  |  |  | 0
| Are all unused conductors grounded in the controller cabinet? | 625.12 |  |  |  |  | 0
| Are the neutral (AC-) and grounding bars in the controller cabinet NOT connected together? | Ground and Bonding Note |  |  |  |  | 0
| Do all empty conduits have a #10 AWG pull wire installed and then have all the ends sealed? | 625.12 |  |  |  |  | 0
| Does the enclosure include a vent, fan, filter and thermostat? | 733.03 |  |  |  |  | 0
| Are all tags or labels properly installed and legible including the service wire, phase numbers and directions? | 632.05
| Are the connectors soldered on the loop lead in wires? | 632.23
| Is all field wiring neatly arranged and routed to prevent being pinched when the cabinet door is closed and free of debris? | 633.08
| Is all wiring (except power) fitted with spade terminals? | 633.08
| Is all power wiring fitted into spade, screw, or spring terminals? | 633.08
| Is there LED lighting in the cabinet? | 733
UPS | [6 empty] | 0
| Does the generator panel work correctly? | 633.18 |  |  |  |  | 0
| Is the controller programmed properly for the UPS alarms? (ON Battery, Battery 2 Hour Timer, Low Battery) | 633.18 |  |  |  |  | 0
Labeling | [6 empty] | 0
| Does each unit have a permanent label or stamp indicating the date of shipment. Controller, Monitor, BIU, 170 and 2070 CPU board, 2070-2A field I/O module, 2070-3B Front Panel. | 733.02.B |  |  |  |  | 0
| Does the warranty period begin on the date of shipment to the project? | 733.02.B |  |  |  |  | 0
Controller Operation and Testing | [6 empty] | 0
| Does the controller call in the proper direction and movement? | 633.06 |  |  |  |  | 0
| Do all movements come in when a call is placed on a loop for that movement? | 633.06 |  |  |  |  | 0
| Do ped push buttons put a call into the controller through the DC isolator? | 633.06 |  |  |  |  | 0
| Does the controller receive the pedestrian call and call in the proper movement? | 633.06 |  |  |  |  | 0
| Are the timings uploaded from the controller per the Planng? | 633.06 |  |  |  |  | 0
| Do the loops work for the assigned detector in the proper phase? | 633.06 |  |  |  |  | 0
| Do the detectors place a call to the controller on the proper phase? | 633.06 |  |  |  |  | 0
Controller Foundation, Work Pad | [6 empty] | 0
| Was the work pad poured separate from the foundation pour? | 633.11 |  |  |  |  | 0
| Is there ½" preformed joint filler between foundation and adjacent paved areas (this includes work pad)? | TC-83.20 |  |  |  |  | 0
Comments Section
Inspection Guidance / Instruction Section
Provide comments for each nonconformance.